Energy Meter VM-3P75CT firmware change log

How to update?
This product can be updated in three ways:

- Using our VictronConnect app, via Ethernet or Wi-Fi. The VM-3P75CT must be connected via Ethernet to your network.

- Update remotely over the internet via our VictronConnect app. Requires a GX-device, such as a Cerbo GX or a Venus GX to be part of the installation.

- Update remotely over the internet via our VRM Portal. Requires a GX-device, such as a Cerbo GX or a Venus GX to be part of the installation.

The VictronConnect app is available for phones, tablets and Windows and macOS laptops. Documentation & download.

Documentation for remote updates via VRM is here.

What firmware version do I currently have?

There are several ways to see the firmware version:

- Look with the VictronConnect app

- Look on your GX Device

- Look at the Device list page on the VRM Portal.

How to configure?

Use the VictronConnect app.

Change log:

v1.11 – 23 September 2025

Note: since v1.09, Venus OS v3.60 or later is required when using VE.Can port as the connection.

Changes/features added:

- Increase robustness of CAN-bus handling to avoid brief passthrough mode occurrences in Multi RS systems.

v1.10 – 27 August 2025

Changes/features added:

- Fix issue where, when connected to less phases than configured for, the meter would produce incorrect readings. Issue was introduced in v1.09.

v1.09 – 12 August 2025

Changes/features added:

- Add power factor and phase sequence reporting. Visible in the GX device, VRM Portal, and the VictronConnect app.

- Reduce required GX Device CPU load when using meters for PV Inverter, AC-load, or other types of metering and connected using VE.Can wiring. The same improvement for Ethernet connected meters was already available per Venus OS v3.60, released before the summer of 2025.

- Add phase rotation warning for 3-phase configuration, visible in the VictronConnect App.

- Improve overall measurements accuracy.

- Fix total power reporting for absolute and arithmetic registration. The most used type of registration, vector, was not affected by the issue.

- Make Ethernet communication more robust.

Known issues:

- Multi-phase configuration with missing phases can lead to incorrect readings, fixed in v1.10.

v1.08 – 11 November 2024

Changes/features added:

- Improve VE.Can communication; this fixes the missing custom name on VenusOS and improves overall stability.

Known issues:

- Wrong total power reporting for absolute and arithmetic registration, fixed in v1.09

v1.07 – Skipped

v1.06 – 19 March 2024

Changes/features added:

- Add LED pulse output to indicate energy flow. Default the LED pulses every 10Wh.

- Several Ethernet-related improvements that should help streamlining the firmware update procedure.

- Update the bootloader to v1.04 to benefit from the same ethernet improvements as mentioned above.

v1.05 – 14 December 2023

Changes/features added:

- Add position setting.

v1.04 – Skipped

v1.03 – 16 October 2023

First version shipped with VictronConnect.

Changes/features added:

- Fix addresses of modbus power registers.

v1.02 – 12 October 2023

Changes/features added:

- Change model name to Energy Meter VM-3P75CT.

- Fix firmware version formatting in mDNS record.

- Fix modbus firmware and hardware version registers.

- Fix factory reset of IP settings.

- Fix polarity of reactive power.

- Fix NMEA2000 ACL procedure getting stuck.

- Fix NMEA2000 fast-packet handling.

- Clamp AC RMS voltage to 327.67V if it exceeds this value.

- Add proper hostname and include in DHCP request and mDNS.

- Add kWh counters.

- Add sign to RMS current.

- Add alternate mapping of modbus measurement registers.

- Enable watchdog.

- Reduce RMS noise of measurements.

- Make factory reset behavior consistent between bootloader and application.

- Issue error and provide recovery mechanism in case of corrupted storage.

v1.01 – 19 July 2023

First approved version for mass production.